## Glossary
Glossary
Sheet: Transformers
| Header | Description
| Transf Type | Transformer type
| V1n [kV] | HV-side nominal voltage
| V2n [kV] | LV-side nominal voltage
| vcc [%] | Short circuit voltage
| pcc [%] | Short circuit power
| Sn [MVA] | Nominal apparent power
Sheet: Lines
| Header | Description
| Line Type | Line type
| Vn [kV] | Nominal voltage
| R [Ohm/km] | Resistance per km
| L [mH/km] | Inductance per km
| C [nF/km] | Capacitance per km
| G [S/km] | Conductance per km
| Imax [A] | Current limit
| R0 [Ohm/km] | Zero-sequence resiistance per km
| L0 [mH/km] | Zero-sequence inductance per km
| C0 [nF/km] | Zero-sequence capacitance per km

## Transformers
Transf Type | vcc [%] | pcc [%] | Sn [MVA]
132/15_40_OLTC | 11.13 | 0.36 | 40

## Lines
Line Type | Vn [kV] | R [Ohm/km] | L [mH/km] | C [nF/km] | Imax [A] | R0 [Ohm/km] | L0 [mH/km] | C0 [nF/km]
UC_AL_120_260 | 15 | 0.2549 | 0.3719 | 400.878 | 260 | 1.7313 | 5.511 | 400.878
UC_AL_150_240 | 15 | 0.2032 | 0.2891 | 360.0355 | 240 | 1.6258 | 5.1751 | 105.0361
UC_AL_150_280 | 15 | 0.2165 | 0.4124 | 420.7208 | 280 | 1.7272 | 5.4978 | 420.7208
UC_AL_185_330 | 15 | 0.1657 | 0.4119 | 451.0565 | 330 | 1.5527 | 4.9425 | 451.0565
UC_AL_240_320 | 15 | 0.1254 | 0.2444 | 419.9205 | 320 | 1.6788 | 5.3438 | 122.0687
UC_AL_240_360 | 15 | 0.1302 | 0.3526 | 499.8661 | 360 | 1.4984 | 4.7696 | 499.8661
UC_CU_100_252 | 15 | 0.1916 | 0.2952 | 304.9127 | 252 | 1.8666 | 5.9416 | 88.8037
UC_CU_120_280 | 15 | 0.1787 | 0.2705 | 323.6873 | 280 | 1.8018 | 5.7354 | 93.878
UC_CU_120_360 | 15 | 0.1504 | 0.3874 | 400.0594 | 360 | 1.5663 | 4.9856 | 400.0594
UC_CU_150_320 | 15 | 0.1314 | 0.2681 | 360.0391 | 320 | 1.6419 | 5.2263 | 105.1026
UC_CU_160_340 | 15 | 0.1214 | 0.2747 | 371.7256 | 340 | 1.5024 | 4.7823 | 108.38
UC_CU_95_245 | 15 | 0.1958 | 0.2667 | 299.8442 | 245 | 1.873 | 5.9619 | 86.8466